# Delhi Jal Board — STP Utilisation Analysis

Source: RTI Act 2005, ID No. 47, dated 08.05.2026 | Analysis updated with all RTI responses

## Aggregate Summary

| Metric | Value |
| --- | --- |
| Total STPs identified | 32 |
| STPs at 100% utilisation | 10 (31.3% of total) |
| STPs overloaded (>100%) | 5 (15.6% of total) |
| STPs underutilised (<100%) | 17 (53.1% of total) |
| Total Installed Capacity (MGD) | 713.6 MGD |
| Total Utilised Capacity (MGD) | 601.51 MGD |
| Overall Utilisation Rate | 84.3% |
| New STPs / upgrades (last 5 yrs) | Yamuna Vihar Ph-II upgraded 2025; Sonia Vihar commissioned 2024; Keshopur Ph-III upgraded 40→60 MGD; Rohini STP +10 MGD (Rs 37.50 Cr) |
| Dual-zone conflicts identified | 2 (Yamuna Vihar: SE-I vs EE-XIII; Rithala: EE-XII vs EE-IX) |
| Plants with NIL O&M (last 5 yrs) | 1 (Rithala Ph-I — under rehabilitation despite 101.7% loading) |

NOTE: Kondli Ph I-IV and Chilla STP (EE-SDW-IV) — RTI response withheld as 'bulky'; utilisation claimed 100% by division but no granular data provided. Figures above use division claim. Independent verification not possible from RTI alone.

## STP-wise Detail: Installed Capacity, Utilisation, O&M and Remarks

| Zone | Division | STP Name | Installed (MGD) | Utilised (MGD) | Rate % | O&M Expenditure (Last 5 Yrs) | Capital Cost | Commissioned | Anomaly / Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SE-I | EE(SDW)-III | Yamuna Vihar Ph-I | 10 (45 MLD) | 2.20 | 22% | Not disclosed | — | Pre-2020 | Severely underutilised. Only 22% capacity used. |
|  |  | Yamuna Vihar Ph-II | 15 (68 MLD) | 3.30 | 22% | Not disclosed | Rs 60.75 Cr (Govt. of India) | 2025 (upgraded +5 MGD) | Upgraded capacity. Severely underutilised. Only 22% capacity used. |
|  |  | Sonia Vihar WWTP | 7.0 (32 MLD) | 0.11 | 1.6% | Not disclosed | Rs 55.70 Cr (GNCT of Delhi) | 2024 | Brand new plant. Severely underutilised. Only 1.6% capacity used despite full capital expenditure. |
| SE-I | EE(SDW)-XIII | Yamuna Vihar (25 MGD) | 25 (114 MLD) | 28-29 | 112-116% | FY22: 4.92 Cr ¦ FY23: 4.83 Cr ¦ FY24: 4.86 Cr ¦ FY25: 5.1 Cr ¦ FY26: 2.7 Cr | — | 2015 | OVERLOADED. Dual-zone conflict: SE-I reports 25 MGD (100%), EE-XIII reports 28-29 MGD actual flow. No CPCB/NGT penalty yet. |
| EE(SDW)-IV | EE(SDW)-IV | Kondli Ph-I | 10 | 10 | 100% | Voluminous — visit office | — | Not disclosed | 100% utilised per division claim. Granular data withheld. |
|  |  | Kondli Ph-II | 25 | 25 | 100% | Voluminous — visit office | — | Not disclosed | 100% utilised per division claim. Granular data withheld. |
|  |  | Kondli Ph-III | 25 | 25 | 100% | Voluminous — visit office | — | Not disclosed | 100% utilised per division claim. Granular data withheld. |
|  |  | Kondli Ph-IV | 45 | 45 | 100% | Voluminous — visit office | — | Not disclosed | 100% utilised per division claim. Granular data withheld. RTI obligation not fully met. |
|  |  | Chilla STP | 9 | 9 | 100% | Voluminous — visit office | — | Not disclosed | 100% utilised per division claim. Granular data withheld. |
| EE(SDW)-XIV | EE(SDW)-XIV | CWG Village Akshardham | 1 (4.55 MLD) | 0.25 | 25% | FY21-26: Rs 83.76 L/yr each year (flat — zero variation; DDA deposit work) | — | 2010 | DDA deposit work — not DJB-owned. Budget by DDA. Flat O&M across 5 years is suspicious. 75% capacity idle. Meets CPCB/DPCC/NGT norms per RTI. |
| EE(SDW)-II | EE(SDW)-II (Okhla) | Okhla 124 MGD | 124 (564 MLD) | 100 | 81% | Voluminous — visit office | Rs 1168 Cr (15% Delhi Govt + 85% Centre) | 2025 | Brand new plant running at only 81%. 24 MGD idle. Parallels Sonia Vihar — massive capital deployed, underutilised from day one. |
|  |  | Okhla 30 MGD | 30 (136 MLD) | 13 | 43% | Voluminous — visit office | — | Not disclosed | 17 MGD idle. Over 50% unused at established STP. |
|  |  | Okhla 16 MGD | 16 (73 MLD) | 7 | 44% | Voluminous — visit office | — | Not disclosed | 9 MGD idle. Over 50% unused. |
| EE(SDW)-V | EE(SDW)-V | Delhi Gate Ph-II | 15 (68 MLD) | 15 | 100% | ~Rs 30 L/month | — | 2016 | Full capacity. No discrepancy. No CPCB/NGT penalty. |
|  |  | Delhi Gate Ph-I | 2.2 (10 MLD) | 2.2 | 100% | Maintained by PPCL (third-party) | — | 1998 | Full capacity. Operated by PPCL. No CPCB/NGT penalty. |
|  |  | SNH | 2.2 (10 MLD) | 2.2 | 100% | Maintained by PPCL (third-party) | — | 1998 | Full capacity. Operated by PPCL. No CPCB/NGT penalty. |
|  |  | Ghitorani | 5.0 (23 MLD) | 3 | 60% | ~Rs 5.50 L/month | — | 2015 | 2 MGD idle. Moderately underutilised. No CPCB/NGT penalty. |
|  |  | Vasant Kunj Ph-I | 2.2 (10 MLD) | 1.75 | 80% | ~Rs 2.95 L/month | — | 1982 | 0.45 MGD spare. Oldest STP in dataset. No CPCB/NGT penalty. |
|  |  | Vasant Kunj Ph-II | 3 (14 MLD) | 2.10 | 70% | ~Rs 1.70 L/month | — | 2001 | 0.9 MGD spare. Moderately underutilised. No CPCB/NGT penalty. |
| EE(SDW)-XI | EE(SDW)-XI | Mehrauli STP | 5 (23 MLD) | 4.99 | 99.8% | FY21: 49.92 L ¦ FY22: 29.99 L ¦ FY23: 131.19 L ¦ FY24: 79.95 L ¦ FY25: 58.70 L | — | 2003 | Near-full utilisation. O&M varies significantly (131.19 L in FY23 vs 29.99 L in FY22 — 4x spike, unexplained). No CPCB/NGT penalty. |
| EE(SDW)-VI | EE(SDW)-VI | Keshopur STP Ph-I | 12 | 12.80 | 107% | Withheld — accounts section | — | Not disclosed | OVERLOADED. 12.80 MGD treated vs 12 MGD design. No new STPs commissioned in last 5 yrs. No CPCB/NGT penalty data provided. |
|  |  | Keshopur STP Ph-II | 20 | 14.12 | 70.6% | Withheld — accounts section | — | Not disclosed | 5.88 MGD idle. Moderately underutilised. |
|  |  | Keshopur STP Ph-III | 60 | 32.17 | 53.6% | Withheld — accounts section | — | Pre-2025 (was 40 MGD; upgraded to 60 MGD) | Capacity upgraded from 40 to 60 MGD before 20.02.2025. Despite upgrade, only 53.6% utilised. 27.83 MGD idle — severe underuse post-upgrade. |
|  |  | Najafgarh STP | 5 | 4.13 | 82.6% | Withheld — accounts section | — | Not disclosed | 0.87 MGD spare. Reasonably utilised. |
|  |  | Nilothi STP-II | 20 | 20.50 | 102.5% | Withheld — accounts section | — | Not disclosed | OVERLOADED. 0.50 MGD above design capacity. Sewage inflow exceeds treatment capacity. |
| EE(SDW)-XII | EE(SDW)-XII | Rohini STP | 25 | 25 | 100% | FY22: 264.42 L ¦ FY23: 904.25 L ¦ FY24: 7035.00 L ¦ FY25: 1385.87 L ¦ FY26: 4168.61 L ¦ Total alloc FY21-26: Rs 21992.25 L; Expended: Rs 13758.15 L | Rs 37.50 Cr (upgrade +10 MGD) | Not disclosed | 100% utilised. Upgraded by 10 MGD. CRITICAL: O&M FY24 = Rs 7035 L (Rs 70.35 Cr) — 5x the next highest year. Massive unexplained spike. Total budget utilisation only 62.5% (13758/21992). |
|  |  | Rithala STP (EE-XII claim) | 40 | 40 | 100% | Same as above (combined O&M for both STPs) | — | Not disclosed | NOTE: EE-XII claims 100% utilisation. EE-IX reports same plant at 40.69 MGD (101.7%). Dual-zone conflict — see EE-IX row below. |
| EE(SDW)-IX | EE(SDW)-IX | Rithala Ph-I (EE-IX claim) | 40 | 40.69 | 101.7% | NIL for last 5 years (plant under rehabilitation) | — | Not disclosed | OVERLOADED. 40.69 MGD vs 40 MGD design. O&M NIL — plant under rehabilitation. DUAL-ZONE CONFLICT with EE-XII which also claims jurisdiction over Rithala STP at 40 MGD/100%. |
| EE(SDW)-VII | EE(SDW)-VII | Coronation Pillar NSTP 70 MGD | 70 | 67.5 | 96.4% | Not disclosed | — | Not disclosed | Utilisation 60-75 MGD range reported. Midpoint 67.5 MGD used. Near-full capacity. |
|  |  | Coronation Pillar NSTP 20 MGD | 20 | 22.5 | 112.5% | Not disclosed | — | Not disclosed | OVERLOADED. Utilisation 20-25 MGD range vs 20 MGD design. Midpoint 22.5 used. |
|  |  | Coronation Pillar NSTP 10 MGD | 10 | 9 | 90% | Not disclosed | — | Not disclosed | Utilisation 8-10 MGD range. Midpoint 9 used. Near-full. |
|  |  | Coronation Pillar NSTP 15 MGD | 15 | 13.5 | 90% | Not disclosed | — | Not disclosed | Utilisation 12-15 MGD range. Midpoint 13.5 used. Near-full. |
| AGGREGATE TOTAL (All STPs) |  |  | 713.6 | 601.51 | 84.3% | 10 at 100% (31.3%) ¦ 5 overloaded >100% (15.6%) ¦ 17 underutilised <100% (53.1%) |  |  |  |

## Key Flags and Gaps

| Flag | Division/STP | Issue | Implication |
| --- | --- | --- | --- |
| OVERLOADED | EE(SDW)-XIII / Yamuna Vihar 25 MGD | 28-29 MGD flow vs 25 MGD installed (112-116%). Dual-zone reporting conflict. | Sewage bypassing treatment. Data manipulation risk between zones. |
| SEVERE UNDERUSE | EE(SDW)-III / Sonia Vihar WWTP | Rs 55.70 Cr plant (2024) running at only 1.6% capacity. | Capital already sunk; sewage still untreated elsewhere while new plant sits idle. |
| SUSPECT O&M | EE(SDW)-XIV / CWG Akshardham | Identical O&M: Rs 83.76 L every year FY21-FY26. Zero variation across 5 years. | Flat figures across 5 years without any variation suggest figures may be copied, not actual. |
| DATA WITHHELD | EE(SDW)-IV / Kondli (all 5 STPs) | Detailed O&M, capital cost, commissioning data declared 'bulky'; applicant directed to visit office. | 114 MGD of capacity unverifiable. RTI obligation not met. |
| DDA OWNERSHIP | EE(SDW)-XIV / CWG Akshardham | STP is DDA deposit work; DJB merely operates. Budget allocated by DDA. | Accountability split between DDA and DJB. Reforms or upgrades require DDA approval. |
| NEW PLANT UNDERPERFORMING | EE(SDW)-II / Okhla 124 MGD | Rs 1168 Cr plant (15% Delhi + 85% Centre) commissioned 2025, running at only 81%. | Same pattern as Sonia Vihar: massive capital spent, plant underutilised from day one. 24 MGD idle. |
| O&M SPIKE | EE(SDW)-XI / Mehrauli STP | O&M jumped from Rs 29.99 L (FY22) to Rs 131.19 L (FY23) — a 4x spike — then dropped to Rs 79.95 L and Rs 58.70 L. No explanation in RTI. | Unexplained expenditure spike warrants audit. No CPCB/NGT penalty, but financial irregularity possible. |
| THIRD-PARTY OPERATOR | EE(SDW)-V / Delhi Gate Ph-I & SNH | Both STPs maintained by PPCL, not DJB directly. | Accountability and performance monitoring rests with contractor. DJB oversight critical. |
| OKHLA IDLE CAPACITY | EE(SDW)-II / Okhla 30 & 16 MGD | Okhla 30 MGD at 43%; Okhla 16 MGD at 44%. Both over 50% idle. O&M data withheld as voluminous. | Combined 26 MGD unused at established STPs. Financial waste compounded by withheld O&M data. |
| O&M SPIKE — CRITICAL | EE(SDW)-XII / Rohini STP | O&M FY24 = Rs 7035 L (Rs 70.35 Cr) vs FY22 = Rs 264.42 L. A 27x spike in one year, then dropped to Rs 1385 L in FY25. | Largest single-year O&M figure in dataset by far. Demands audit. No explanation in RTI. Budget utilisation only 62.5% overall despite the spike. |
| DUAL-ZONE CONFLICT | EE(SDW)-XII & EE(SDW)-IX / Rithala STP | EE-XII claims Rithala STP (40 MGD) at 100%. EE-IX claims Rithala Ph-I (40 MGD) at 40.69 MGD (101.7%). Two divisions claiming same plant. | Same pattern as Yamuna Vihar dual-zone conflict. Installed capacity effectively counted twice in aggregate. Real utilisation figure unclear. |
| PLANT UNDER REHABILITATION | EE(SDW)-IX / Rithala Ph-I | O&M declared NIL for last 5 years — plant under rehabilitation. Yet utilisation reported at 40.69 MGD (101.7% overloaded). | Overloaded plant with zero O&M spend for 5 years. Structural/operational integrity risk. Sewage being treated with no maintenance budget. |
| POST-UPGRADE UNDERUSE | EE(SDW)-VI / Keshopur Ph-III | Capacity upgraded from 40 to 60 MGD (added 20 MGD). Actual utilisation only 32.17 MGD — 53.6% of new capacity. | Upgrade investment wasted. 27.83 MGD idle post-expansion. No capital cost disclosed for the upgrade. |
| OVERLOADED ×4 | Keshopur Ph-I / Nilothi-II / Yamuna Vihar / Coronation 20 MGD | 4 additional plants now confirmed overloaded: Keshopur Ph-I (107%), Nilothi-II (102.5%), Coronation 20 MGD (112.5%), plus existing Yamuna Vihar XIII (114%) and Rithala Ph-I (101.7%). | Total 6 plants overloaded across dataset. Untreated sewage overflow systematic, not isolated. |

Data Sources: RTI Act 2005. Responses received from: EE(SDW)-III (19.05.2026), EE(SDW)-XIII (13.05.2026), EE(SDW)-XIV (08.05.2026), EE(SDW)-IV/Kondli (11.05.2026), EE(SDW)-II/Okhla (batch 2), EE(SDW)-V/Andrews Ganj (batch 2), EE(SDW)-XI/Kilokri (batch 2), EE(SDW)-VI/Keshopur-Najafgarh (24.03.2026), EE(SDW)-XII/Rohini (28.03.2026), EE(SDW)-IX/Rithala Ph-I (12.03.2026), EE(SDW)-VII/Coronation Pillar (27.03.2026). EE(SDW)-I confirmed no STP under jurisdiction. NOTE: EE-VII utilisation figures reported as ranges; midpoints used for calculations. Rithala STP counted once in aggregate (EE-IX figure used); EE-XII claim flagged as duplicate.